Retractable Chemical Injection Assembly Specifications 
Section 11XXX
Retractable Chemical Injection Assembly:
1.  Rating 150 psi.

2.  Type: Insertion type injection quill.

3.  Connection:  Connect to process pipe using service saddle and ball valve
4.  Construction:

Injection assembly shall come complete with ball valve, solution tube, solution tube adapter, packing nut, safety chain and threaded inlet connection.

Solution tube shall be for sufficient length to extend into the process pipe to between one third and one half the pipeline diameter.
Injector should allow for rodding in place.

Connection must include an acceptable safety device to prevent accidental withdrawal of injection solution tube while under pressure and/or surge conditions.  All wetted components shall be compatible with the chemical services.

5.  Chemical Injection Assembly should be Model #”______” by Inyo Process or equal preapproved by the engineer.
